## Grid
[16 empty] | Column |  | A | B | C | D | E | F | G | H | I | P | Q | L | M | J | K | N | O
[18 empty] | Blow Down Valve Solenoid (SY-2405) | Compressor #1 (K-2400) Main Motor Run Command | Compressor #1 (M-2480) Cooler Fan Motor Run Command | Compressor #1 (K-2400) Compressor Run Status | Compressor #1 (K-2400) Alarm Status | Compressor #2 (K-2410) Main Motor Run Command | Compressor #2 (M-2490) Cooler Fan Motor Run Command | Compressor #2 (K-2410) Compressor Run Status | Compressor #2 (K-2410) Alarm Status | M-2440 Glycol Pump Motor Run Command | M-2450 Glycol Pump Motor Run Command | Recycle/Bypass Control Valve I/P | Back Pressure Control Valve | Compressor #1 Speed Control | Compressor #2 Speed Control | Air Cooler Fan Speed Control (M-2480) | Air Cooler Fan Speed Control (M-2490)
| Spirit River VRU Compressor | [6 empty] | LEGEND
[8 empty] | SP | STOP
| SHUTDOWN KEY | [6 empty] | ST | START
| No. | Revison | Project | By | Date | Chk | App | OP | OPEN
| A |  |  | AK | JAN 17TH 2015 |  |  | OP | OPEN
[8 empty] | CL | CLOSE
[8 empty] | TD | TIME DELAY
[8 empty] | RS | RESET
[8 empty] | P | PERMISSIVE
[8 empty] | CTRL | CONTROL
Description
Engineering Stamps
Standard Shutdowns
[11 empty] | ALARM | INDICATION | RESET | PROCESS SHUTDOWN 1 | PROCESS SHUTDOWN 2 | Soft | Tag
[18 empty] | SY-2405 | UC-2400-1 | UC-2480-1 | US-2400-1 | UA-2400-1 | US-2410-2 | UC-2490-1 | US-2410-1 | UA-2410-1 | UC-2440-1 | UC-2450-1 | PY-2404 | BPCV-2403 | SY-2400 | SY-2410 | SY-2480 | SY-2490
[16 empty] | Hard | Tag
[16 empty] | PLC | Output | O:01.0/0 | O:01.0/4 | O:01.0/5 | O:01.0/6 | O:01.0/7 | O:01.0/8 | O:01.0/9 | O:01.0/10 | O:01/11 | O:01.0/14 | O:01.0/15 | O:02.0/0 | O:02.0/01 | O:02.0/2 | O:02.0/3 | O:02.0/04 | O:02.0/05
[7 empty] | Standard Shutdowns | ALARM |  |  | X
[8 empty] | INDICATION |  |  |  | X
[8 empty] | RESET |  |  |  |  | X
[8 empty] | PROCESS SHUTDOWN 1 | [5 empty] | X
[8 empty] | PROCESS SHUTDOWN 2 | [6 empty] | X
[8 empty] | Hard | Soft | PLC | [5 empty] | Column |  | A | B | C | D | E | F | G | H | I | P | Q | L | M | J | K | N | O
Row | Description | [6 empty] | Tag | Tag | Input | [5 empty] | Row | [18 empty] | Remarks
1 | Inlet Separator Level High (V-2400) | [6 empty] | LSH-2400 |  | Local:6:I.Data.0 | X |  | X |  |  |  | 1 | bar: B to C; F to G; P to Q
2 | Oil/Gas Separator Level Low (V-2420) | [6 empty] | LSL-2420 |  | Local:6:I.Data.1 | X |  | X |  |  |  | 2 | bar: B to C; P
3 | Oil/Gas Separator Level High (V-2420) | [6 empty] | LSH-2420 |  | Local:6:I.Data.2 | X |  | X |  |  |  | 3
4 | Glycol tank Level Low (T-2440) | [6 empty] | LSL-2440 |  | Local:6:I.Data.3 | X | X | X |  |  |  | 4 | bar: B to C; P
5 | Oil/Gas Separator Level Low (V-2430) | [6 empty] | LSL-2430 |  | Local:6:I.Data.4 | X |  | X |  |  |  | 5 | bar: F to G; Q
6 | Oil/Gas Separator Level High (V-2430) | [6 empty] | LSH-2430 |  | Local:6:I.Data.5 | X | X | X |  |  |  | 6
7 | Glycol tank Level Low (T-2450) | [6 empty] | LSL-2450 |  | Local:6:I.Data.6 | X | X | X |  |  |  | 7 | bar: F to G; Q
8 | Main motor Run Status (M-2400) | [6 empty] | US-2400-2 |  | Local:7:I.Data.7 |  | X |  |  |  |  | 8 | bar: D
9 | Glycol Pump motor Run Status (M-2440) | [6 empty] | US-2440-2 |  | Local:7:I.Data.8 | X | X | X |  |  |  | 9
10 | Cooler Fan motor Run Status (M-2480) | [6 empty] | US-2480-2 |  | Local:7:I.Data.9 | X | X | X |  |  |  | 10
11 | Main motor Run Status (M-2410) | [6 empty] | US-2410-2 |  | Local:7:I.Data.10 |  | X |  |  |  |  | 11 | bar: H
12 | Glycol Pump motor Run Status (M-2450) | [6 empty] | US-2450-2 |  | Local:7:I.Data.11 | X | X | X |  |  |  | 12
13 | Cooler Fan motor Run Status (M-2490) | [6 empty] | US-2490-2 |  | Local:7:I.Data.12 | X | X | X |  |  |  | 13
14 | Remote Stop | [6 empty] | USC-2400 |  | Local:7:I.Data.13 | X | X | X |  |  |  | 14 | bar: B to C; F to G; P to Q
15 | Remote Emergency Shutdown | [6 empty] | USE-2400 |  | Local:7:I.Data.14 | X | X | X |  |  |  | 15 | bar: A to C; F to G; P to Q
16 | K-2400 / K2410 Panel Emergency Shutdown | [6 empty] | ESD-2400 |  | Local:7:I.Data.15 | X | X | X |  |  |  | 16 | bar: A to C; F to G; P to Q
#REF! | Tank Vapour Header Pressure Low Low (V-2400) | [6 empty] | PIT-2400 |  | Local:3:I.Ch0Data | X | X | X |  |  |  | #REF! | bar: B to C; F to G; P to Q
#REF! | Tank Vapour Header Pressure Low (V-2400) | [6 empty] | PIT-2400 |  | Local:3:I.Ch0Data | X |  | X |  |  |  | #REF! | bar: E; I
#REF! | Tank Vapour Header Pressure High (V-2400) | [6 empty] | PIT-2400 |  | Local:3:I.Ch0Data | X |  | X |  |  |  | #REF! | bar: E; I
#REF! | Tank Vapour Header Pressure Transmitter Fail (V-2400) | [6 empty] | PIT-2400 |  | Local:3:I.Ch0Data | X |  | X |  |  |  | #REF! | bar: B to C; F to G; P to Q
#REF! | Tank Vapour Header Pressure (V-2400) | [6 empty] | PIT-2400 |  | Local:3:I.Ch0Data | X |  | X |  |  |  | #REF! | L: CTRL
#REF! | Suction Pressure High (K-2400) | [6 empty] | PIT-2400A |  | Local:3:I.Ch1Data | X |  | X |  |  |  | #REF! | bar: E
#REF! | Suction Pressure Low (K-2400) | [6 empty] | PIT-2400A |  | Local:3:I.Ch1Data | X |  | X |  |  |  | #REF! | bar: E
#REF! | Suction Pressure Low Low (K-2400) | [6 empty] | PIT-2400A |  | Local:3:I.Ch1Data | X | X | X |  |  |  | #REF! | bar: B to C; P
#REF! | Suction Pressure Transmitter (K-2400) | [6 empty] | PIT-2400A |  | Local:3:I.Ch1Data | [6 empty] | #REF! | J: CTRL
#REF! | Discharge Pressure Low (K-2400) | [6 empty] | PIT-2400B |  | Local:3:I.Ch2Data |  | X |  |  |  |  | #REF! | bar: E
#REF! | Discharge Pressure (K-2400) | [6 empty] | PIT-2400B |  | Local:3:I.Ch2Data |  | X |  |  |  |  | #REF! | M: CTRL
#REF! | Discharge Pressure High (K-2400) | [6 empty] | PIT-2400B |  | Local:3:I.Ch2Data |  | X |  |  |  |  | #REF! | bar: E
#REF! | Discharge Pressure High High (K-2400) | [6 empty] | PIT-2400B |  | Local:3:I.Ch2Data | X |  | X |  |  |  | #REF! | bar: B to C; P
#REF! | Gas Differential Pressure Low Low (K-2400) | [6 empty] | DPT-2400 |  | Local:3:I.Ch3Data | X |  | X |  |  |  | #REF! | bar: B to C; P
#REF! | Gas Differential Pressure Low (K-2400) | [6 empty] | DPT-2400 |  | Local:3:I.Ch3Data | [6 empty] | #REF!
#REF! | Oil Filter Differential Pressure High (V-2420) | [6 empty] | DPT-2420 |  | Local:3:I.Ch4Data | X |  | X |  |  |  | #REF! | bar: E
#REF! | Oil Filter Differential Pressure High High (V-2420) | [6 empty] | DPT-2420 |  | Local:3:I.Ch4Data | X | X | X |  |  |  | #REF! | bar: B to C; P
#REF! | Gas Discharge Temperature (E-2480) | [6 empty] | TIT-2400A |  | Local:3:I.Ch5Data |  | X |  |  |  |  | #REF! | N: CTRL
#REF! | Discharge Temperature High (K-2400) | [6 empty] | TIT-2400B |  | Local:3:I.Ch6Data | X | X | X |  |  |  | #REF! | bar: E
#REF! | Discharge Temperature High High (K-2400) | [6 empty] | TIT-2400B |  | Local:3:I.Ch6Data | X | X | X |  |  |  | #REF! | bar: B to C; P
#REF! | Glycol Temperture High (K-2400) | [6 empty] | TT-2440 |  | Local:3:I.Ch7Data | X |  | X |  |  |  | #REF! | bar: E
#REF! | Glycol Temperture High High (K-2400) | [6 empty] | TT-2440 |  | Local:3:I.Ch7Data | X |  | X |  |  |  | #REF! | bar: B to C; P
#REF! | Suction Pressure High (K-2410) | [6 empty] | PIT-2410A |  | Local:4:I.Ch0Data |  |  | X |  |  |  | #REF! | bar: I
#REF! | Suction Pressure Low (K-2410) | [6 empty] | PIT-2410A |  | Local:4:I.Ch0Data | X |  | X |  |  |  | #REF! | bar: I
#REF! | Suction Pressure Low Low (K-2410) | [6 empty] | PIT-2410A |  | Local:4:I.Ch0Data | X |  | X |  |  |  | #REF! | bar: F to G; Q
#REF! | Suction Pressure Transmitter (K-2410) | [6 empty] | PIT-2410A |  | Local:4:I.Ch0Data | [6 empty] | #REF! | K: CTRL
#REF! | Discharge Pressure (K-2410) | [6 empty] | PIT-2410B |  | Local:4:I.Ch1Data |  | X |  |  |  |  | #REF!
#REF! | Discharge High Pressure (K-2410) | [6 empty] | PIT-2410B |  | Local:4:I.Ch1Data | X |  | X |  |  |  | #REF! | M: CTRL
#REF! | Discharge High High Pressure (K-2410) | [6 empty] | PIT-2410B |  | Local:4:I.Ch1Data | X |  | X |  |  |  | #REF! | bar: F to G; I; Q
#REF! | Gas Differential Pressure Low Low (K-2410) | [6 empty] | DPT-2410 |  | Local:4:I.Ch2Data | X |  | X |  |  |  | #REF! | bar: F to G; Q
#REF! | Gas Differential Pressure Low (K-2410) | [6 empty] | DPT-2410 |  | Local:4:I.Ch2Data | X |  | X |  |  |  | #REF! | bar: I
#REF! | Oil Filter Differential Pressure High (V-2430) | [6 empty] | DPT-2430 |  | Local:4:I.Ch3Data | X |  | X |  |  |  | #REF! | bar: I
#REF! | Oil Filter Differential Pressure High High (V-2430) | [6 empty] | DPT-2430 |  | Local:4:I.Ch3Data | X | X | X |  |  |  | #REF! | bar: F to G; Q
#REF! | Gas Discharge Temperature (E-2490) | [6 empty] | TIT-2410A |  | Local:4:I.Ch4Data |  | X |  |  |  |  | #REF! | O: CTRL
#REF! | Discharge Temperature High (K-2410) | [6 empty] | TIT-2410B |  | Local:4:I.Ch5Data | X | X | X |  |  |  | #REF! | bar: I
#REF! | Discharge Temperature High High (K-2410) | [6 empty] | TIT-2410B |  | Local:4:I.Ch5Data | X | X | X |  |  |  | #REF! | bar: F to G; Q
#REF! | Glycol Temperture High (K-2410) | [6 empty] | TT-2450A |  | Local:4:I.Ch6Data | X |  | X |  |  |  | #REF! | bar: I
#REF! | Glycol Temperture High High(K-2410) | [6 empty] | TT-2450A |  | Local:4:I.Ch6Data | X |  | X |  |  |  | #REF! | bar: F to G; Q
[18 empty] | A | B | C | D | E | F | G | H | I | P | Q | L | M | J | K | N | O
NOTES: